## Slide 1: Physical Assets Supporting Science
AOML Infrastructure Overview
LCDR Andrew Colegrove, NOAA
AOML Associate Director

## Slide 2: AOML Infrastructure Overview
Current Status
  Main Building, Warehouse, Small Boats, Mobile Containers
Existing Issues
  Aging facility, lack of modern technology
Preparing for the Future
  Immediate (1 Year), Short Term (3 Year), Long Term (Beyond 3 Year)

## Slide 3: Main Building
Commissioned in 1973
40 year life span
NOAA/OAR owned
57,000 usable sqft
  27,000 office (47%)
  2,690 lab (6%)
Lab Spaces
  Water Quality, Core, Inorganic Chem, Ammonia, Micro Biology, Chlorophyll
1973

## Slide 4: Warehouse
Built 1989
30 year roof life span
10,000 sq. ft.
Multi-level shelving
Multiple storage bays
Not climate controlled
Approaching roof end-of-life

## Slide 5: Small Boats
R/V Cable
  21’ Parker
  Built: 1990
R/V GBN1
  25’ Dusky
  Built: 2018
R/V Whipray
  22’ JB
  Built: 2014

## Slide 6: Small Boats
R/V Cable
  21’ Parker
  Built: 1990
R/V GBN1
  25’ Dusky
  Built: 2018
R/V Whipray
  22’ JB
  Built: 2014

## Slide 7: Exterior Containers
Expanding needs
  Cold sample storage
  Gliders
  Buoys
5
6
1
A/C Containers
Storage Containers
Occupiable trailer
2
Mobile Labs
Notes: 5 - A/C containers
6 - Storage containers
1 - Occupiable trailer
2 - Mobile Labs (ships)

## Slide 8: Existing Issues
Utilities
Failing Roof Systems
HVAC
Water Pressure
Emergency Power
Data & Comms
High Speed Network Systems
Data Center Damage
UPS Clean Power
Code Compliance
Fire Sprinkler System
Modernization
Aging Labs
Lack of Storage
Failing Lab Systems
Wall & Ceiling Deterioration
1
2
3
4

## Slide 9: Utilities
Roof Systems
  End of lifespan, failing at seams and penetrations
HVAC
  Aged & inefficient
  Leaking condensation
Water Pressure
  Failed Lift station pump
Emergency Power
  No functional or sufficient source of back-up power

## Slide 10: Data & Comms
High Speed Data Needs
  Facility re-cabling
  High speed backbone
Data Center Damage
  Poor facility placement
  Faulty roll-up doors
UPS Clean Power
  Provide clean power to data center & labs

## Slide 11: Code Compliance
Sprinkler System
  Required for renovations
  Needed for whole facility

## Slide 12: Modernization
Failing Lab Systems
Fume hoods, clean power
Aging Labs
Utilities, work surfaces, sink basins, drainage, lighting
Lack of Storage
Lab space used for storage
Utilizing exterior A/C containers is inefficient and costly
Wall & Ceiling Deterioration Throughout the facility
Notes: Failing Lab Systems
  Fume hoods, clean power
Aging Labs
  Utilities, work surfaces, sink basins, drainage, lighting
Lack of Storage
  Lab space used for storage
  Utilizing exterior A/C containers is inefficient and costly
Wall & Ceiling Deterioration
  Throughout the facility

## Slide 13: Preparing for the Future
Immediate Plan (FY20)
Critical Facility Needs
  Keeping the weather outside
  Hurricane Damage Repair & Prevention
  Main Roof Replacement
  HVAC replacement
  Fire Sprinkler System
  E-Power Backup
Short-Term Plan (FY20 - FY22)
Updating Workspaces & facility capabilities
  Fume Hood Replacement
  Wall & ceiling resurfacing
  Renovate office spaces
  IT/Data re-cable
  UPS Clean Power
  VAV Climate Control
Long-Term Plan (Beyond FY22)
Infrastructure Improvements
  Warehouse rebuild or renovate for A/C
  Renovate laboratory spaces
  Conference & meeting room renovations
  Workshop renovations
1
2
3

## Slide 14: Accomplishments So Far
Admin Space Renovation
  Updated meeting room
  Large common administrative space
PhOD Engineering Renovation
  Significant functional improvement
  New meeting space
  Supports Glider engineering
Experimental Coral Lab at RSMAS
Exterior pathway lighting

## Slide 15: Powering the Science
Need Direct Access to Ocean Water
  Coral reef restoration
  Local event response
  SEFSC Partnership
Potential for High Performance Computing
  Support AI research
  Aligns with OCIO HPC Strategic Plan
  Support HRD real-time data needs
Small Boat Improvements
  Increase survey distance beyond 20nm
  Increase scientific reach & capability

## Slide 16
THANK YOU
Questions?